## WEATHER
Design Heating T | 20
Design Cooling T | 24
Summer T | 31.9
Winter T | -4.8
DR | 11.8
Latitude | 45
Ground T | 20
Ground T Amplitude | 0

## INPUT_WINDOWS
Name | Orientation | Fix/Oper | ID | Frame | Height | Width | Exterior Attachment | Fcl | Glazing Type | Glazing Layers | Drape type | Overhang Depth | Overhang height
E1 | E | F | 5c | W | 1.8 | 8 | None | 0.4 | 2 | 2 | 1 | 0.9 | 0.3
W1 | W | F | 5c | W | 1.8 | 8 | None | 0.4 | 2 | 2 | 1 | 0.9 | 0.3
S1 | S | F | 5c | W | 1.8 | 2 | None | 0.4 | 2 | 2 | 1 | 0.9 | 0.3
S2 | S | O | 5c | W | 1.8 | 2 | Insect | 0.4 | 2 | 2 | 1 | 0.9 | 0.3
n | n | n | n | n | n | n
PLEASE CHECK THE 'WindowInfo' SHEET TO SELECT THE WINDOWS | [8 empty] | This is for interior Atenuation calculation
IF THE NAME IS 'n' THE CODE WILL NOT CONSIDER THAT ROW |  |  |  |  | Orientation List |  |  | Glazing Type List |  | Drape Type List
[5 empty] | N | north |  | 1 | Clear | 1 | Light-Open Weave
ID LIST |  | Frame LIST |  |  | NE | north east |  | 2 | Heat absorbing | 2 | Dark - Closed Weave
1a |  | A | Aluminum |  | NW | north west |  | 3 | Low e high solar | 3 | Light- Closed Weave
5a |  | AT | Aluminum with Thermal Break |  | E | east |  | 4 | Low e low solar
29a |  | RA | Reinforced Aluminum Clad Wood |  | W | west
25a |  | W | Wood/Vinyl |  | SE | south east |  | Glazing Layers List
40c |  | IF | Insulated Fiberglass/Vinyl |  | SW | soth west |  | 1 | single
17c |  |  |  |  | S | south |  | 2 | double
32c |  | Type LIST |  |  | H | Horizontal
1c |  | F | FIXED
5c |  | O | OPERABLE |  | Exterior Attachment List
29c |  |  |  |  | None
1l |  |  |  |  | Insect
5p
29c

## WindowInfo
|  |  | U_FACTORS OPERABLE FENESTRATION | [8 empty] | SHGC OPERABLE FENESTRATION
Type | Glazing | ID | Aluminum | Aluminum with Thermal Break | Reinforced Aluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl | Type | Glazing | ID | Aluminum | Aluminum with Thermal Break | Reinforced Aluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl
Type | Glazing | ID | A | AT | RA | W | IF | Type | Glazing | ID | A | AT | RA | W | IF
Clear | 1 | 1a | 7.24 | 6.12 | 5.14 | 5.05 | 4.61 | Clear | 1 | 1a | 0.75 | 0.75 | 0.64 | 0.64 | 0.64
| 2 | 5a | 4.62 | 3.42 | 3.00 | 2.87 | 5.83 |  | 2 | 5a | 0.67 | 0.67 | 0.57 | 0.57 | 0.57
| 3 | 29a | 3.80 | 2.60 | 2.25 | 2.19 | 1.91 |  | 3 | 29a | 0.60 | 0.60 | 0.51 | 0.51 | 0.51
Low-e,low-solar | 2 | 25a | 3.83 | 2.68 | 2.33 | 2.21 | 1.89 | Low-e,low-solar | 2 | 25a | 0.37 | 0.37 | 0.31 | 0.31 | 0.31
| 3 | 40c | 3.22 | 2.07 | 1.76 | 1.71 | 1.45 |  | 3 | 40c | 0.25 | 0.25 | 0.21 | 0.21 | 0.21
Low-e,high-solar | 2 | 17c | 4.05 | 2.89 | 2.52 | 2.39 | 2.07 | Low-e,high-solar | 2 | 17c | 0.62 | 0.62 | 0.52 | 0.52 | 0.52
| 3 | 32c | 3.54 | 2.36 | 2.02 | 1.97 | 1.70 |  | 3 | 32c | 0.55 | 0.55 | 0.46 | 0.46 | 0.46
Heat-absorbing | 1 | 1c | 7.24 | 6.12 | 5.14 | 5.05 | 4.61 | Heat-absorbing | 1 | 1c | 0.64 | 0.64 | 0.54 | 0.54 | 0.54
| 2 | 5c | 4.62 | 3.42 | 3.00 | 2.87 | 2.53 |  | 2 | 5c | 0.55 | 0.55 | 0.46 | 0.46 | 0.46
| 3 | 29c | 3.80 | 2.60 | 2.25 | 2.19 | 1.91 |  | 3 | 29c | 0.31 | 0.31 | 0.26 | 0.26 | 0.26
Reflective | 1 | 1l | 7.24 | 6.12 | 5.14 | 5.05 | 4.61 | Reflective | 1 | 1l | 0.28 | 0.28 | 0.24 | 0.24 | 0.24
| 2 | 5p | 4.62 | 3.42 | 3.00 | 2.87 | 2.53 |  | 2 | 5p | 0.27 | 0.27 | 0.22 | 0.22 | 0.22
| 3 | 29c | 3.80 | 2.60 | 2.25 | 2.19 | 1.91 |  | 3 | 29c | 0.31 | 0.31 | 0.26 | 0.26 | 0.26
|  |  | U_FACTORS FIXED FENESTRATION | [8 empty] | SHGC FIXED FENESTRATION
Type | Glazing | ID | Aluminum | Aluminum with Thermal Break | Reinforced Aluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl | Type | Glazing | ID | Aluminum | Aluminum with Thermal Break | ReinforcedAluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl
Type | Glazing | ID | A | AT | RA | W | IF | Type | Glazing | ID | A | AT | RA | W | IF
Clear | 1 | 1a | 6.42 | 6.07 | 5.55 | 5.55 | 5.35 | Clear | 1 | 1a | 0.78 | 0.78 | 0.75 | 0.75 | 0.75
| 2 | 5a | 3.61 | 3.22 | 2.86 | 2.84 | 2.72 |  | 2 | 5a | 0.69 | 0.69 | 0.67 | 0.67 | 0.67
| 3 | 29a | 2.76 | 2.39 | 2.05 | 2.01 | 1.93 |  | 3 | 29a | 0.62 | 0.62 | 0.60 | 0.60 | 0.60
Low-e,low-solar | 2 | 25a | 2.75 | 2.36 | 2.03 | 2.01 | 1.90 | Low-e,low-solar | 2 | 25a | 0.38 | 0.38 | 0.36 | 0.36 | 0.36
| 3 | 40c | 2.13 | 1.76 | 1.44 | 1.40 | 1.33 |  | 3 | 40c | 0.25 | 0.25 | 0.24 | 0.24 | 0.24
Low-e,high-solar | 2 | 17c | 2.99 | 2.60 | 2.26 | 2.24 | 2.13 | Low-e,high-solar | 2 | 17c | 0.64 |  | 0.61 | 0.61 | 0.61
| 3 | 32c | 2.47 | 2.10 | 1.77 | 1.73 | 1.66 |  | 3 | 32c | 0.56 | 0.56 | 0.54 | 0.54 | 0.54
Heat-absorbing | 1 | 1c | 6.42 | 6.07 | 5.55 | 5.55 | 5.35 | Heat-absorbing | 1 | 1c | 0.66 | 0.66 | 0.64 | 0.64 | 0.64
| 2 | 5c | 3.61 | 3.22 | 2.86 | 2.84 | 2.72 |  | 2 | 5c | 0.56 | 0.56 | 0.54 | 0.54 | 0.54
| 3 | 29c | 2.76 | 2.39 | 2.05 | 2.01 | 1.93 |  | 3 | 29c | 0.31 | 0.31 | 0.30 | 0.30 | 0.30
Reflective | 1 | 1l | 6.42 | 6.07 | 5.55 | 5.55 | 5.35 | Reflective | 1 | 1l | 0.29 | 0.29 | 0.27 | 0.27 | 0.27
| 2 | 5p | 3.61 | 3.22 | 2.86 | 2.84 | 2.72 |  | 2 | 5p | 0.27 | 0.27 | 0.26 | 0.26 | 0.26
| 3 | 29c | 2.76 | 2.39 | 2.05 | 2.01 | 1.93 |  | 3 | 29c | 0.31 | 0.31 | 0.30 | 0.30 | 0.30

## INPUT_OPAQUE
Summer(1) Winter(2) | 1
Ceiling adjacent to Attic : Yes(1) No(2) | 1
Walls Exposed(1) Shaded (2) | 1
Floor positioned over Ambient(1) CrawlSpace(2) | 1
Door Exposed(1) Shaded(2) | 1
IMPORTANT
The areas of Walls, Ceiling , Floors and Doors must be modified Directly in the sheet RESULTS_OPAQUE

## INPUT_WALLS
Layers | Thickness (mm) | percentage | Layers | Thickness (mm) | Percentage | ID
gypsum | 13 | 0.3 | gypsum | 13 | 0.7 | out_winter
wood_stud_2.4 | 90 |  | glass_fiber | 90 |  | out_summer
wood_bevel | 13 |  | wood_bevel | 13 |  | ins
wood_fiber | 13 |  | wood_fiber | 13 |  | air_space_13
com_brick | 100 |  | com_brick | 100

## INPUT_CEILING
Uceiling | 0.25
color | medium
material | asphalt

## INPUT_FLOOR
Layers | Thickness (mm)
cement | 52
glass_fiber | 50
asphalt | 400
slag | 26

## INPUT_DOOR
Layers | Thickness (mm)
wood | 25
wood | 25

## INPUT_BELOW
BELOW GRADE DATA |  | For the ground floor type use:
z2 | 1.8 | 1 | 200 mm block wall, brick facing
Wall Resistance | 0.259 | 2 | 100 mm block wall, brick facing
Width1 | 12.5 | 3 | Metal stud wall, stucco
Width2 | 22.5 | 4 | Poured concrete wall with duct near perimeter
T inside | 20
T mean ground | 20
T ground amplitude | 0 | NO NEED TO MODIFY, THE CODE TAKES IT FROM WEATHER DATA
z1 | 1
Uninsulation resistance | 0.94
Ground floor type | 2
Is the groud floor insulated? (Y/N) | N
Internal temperature of the building | 20

## INPUT_INFVENT
Volume [m3] | 480
Exposed Surface Area [m2] | 344
Type of construction [-] | Average
Design condition [Cooling/Heating] | boh
Average Stack Height [m] | 2.4
Outdoor Temperature , HEATING [°C] | -4.8
Outdoor Temperature, COOLING [°C] | 31.9
Effective Leakage Area [cm2] | 0 | <------ | for semplicity take it equal to zero
Building conditioned floor area [m2] | 200
Number of bedrooms [-] | 1
Ventilation supply air floor rate [l/s] | 0
Ventilation exhaust air floor rate [l/s] | 0
Air sensible heat factor_Cs [W/l*s*K] | 1.23
HRV/ERV Sensible effectiveness [-] | 0
Balanced ventilation flow rate [l/s] | 0
Other balanced ventilation supply flow rate [l/s] | 0
HRV/ERV [y/n] | ciao
Air latent heat factor_Cl [W/l*s] | 3010
Indoor/Outdoor humidity ratio difference [kg/kg] | 0.0039
Air total heat factor_Ct [W/l*s] | 1.2
HRV/ERV total effectiveness [-] | 0
Indoor/Outdoor enthalpy difference [kJ/kg] | 0

## INPUT_DISTRIBUTION
| Type the desired option |  |  | OPTIONS
Duct Location | Attic | Attic | Basement | Crawlspace | Conditioned space
Insulation [m2.K/W] | 1.4 | 1.2
Suppy/Return Leakage | 5 | 5 | 11
Cooling Conditioning Type | C | C
Heating Conditioning Type | H/F | H/F | H/HP
Number of Stories | 1 | 1 | 2

## RESULTS_WINDOWS
Name | Area | IAC | PXI | HF | CF | Heating Load [W] | Cooling Load [W]
E1 | 14.4 | 0.892 | 560.6667 | 70.432 | 90.7397 | 1014.2208 | 1306.6513
W1 | 14.4 | 0.892 | 560.6667 | 70.432 | 158.2552 | 1014.2208 | 2278.8742
S1 | 3.6 | 0.892 | 209 | 70.432 | 54.3359 | 253.5552 | 195.6093
S2 | 3.6 | 0.892 | 133.76 | 71.176 | 32.8903 | 256.2336 | 118.4051
n | n | n | n | n | n | n | n
[5 empty] | TOTAL | 2538.2304 | 3899.5399

## RESULTS_OPAQUE
Component | area | U | alpha roof | DR value | HF | Q_heating | CF | Q_cooling
Roof/Ceiling | 200 | 0.25 | 0.85 | 11.8 | 6.2 | 1240 | 2.5777 | 515.55
Exterior Walls | 105.8 | 0.4385 | UwallHeating |  | 10.8749 | 1150.5618 | 5.1971 | 549.8572
Doors | 2.2 | 2.2727 |  |  | 56.3636 | 124 | 26.9364 | 59.26
Floor | 0 | 0.56818 |  |  | 14.0909 | 0 | 4.7898 | 0
Exterior Walls | 105.8 | 0.43529 | UwallCooling |  | 10.7952 | 1142.1279 | 5.159 | 545.8266

## RESULTS_BELOW
Below Walls Loss [W] | 0 | U wall [w/m2.K] | 0.63691 | Area wall [m2] | 126
Below Floor Loss [W] | 0 | U Floor [w/m2.K] | 0.14031 | Area Floor [m2] | 281.25
Roof Loss [W] | 0 | N/A | 0 | N/A | 0
Total Heat Loss [W] | 0 | N/A | 0 | N/A | 0

## RESULTS_INFVENT
Average Leakage Area [cm^2] | 963.2
Infiltration Driving Force cooling [L/(s*cm^2)] | 0.032205
Infiltration Driving Force heating [L/(s*cm^2)] | 0.071832
Required Ventilation Flow Rate [L/s] | 17
Infiltration Rate Cooling [L/s] | 31.0197
Infiltration Rate Heating [L/s] | 69.1886
Sensible Infiltration/Ventilation Cooling Load [W] | 466.6071
Sensible Infiltration/Ventilation Heating Load [W] | 2629.0965
Latent Infiltration/Ventilation Load [W] | 563.7028
Internal Gain, sensible [W] | 620
Internal Gain, latent [W] | 88

## RESULTS_DISTRIB
2 | 2
Heating distribution losses | 998.6455
Cooling distribution losses | 1648.8316
2 | 2
2 | 2

## Typical_Duct_Loss
Typical Duct Loss/Gain Factors
|  | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
| Supply/Return Leakage | 11 | 11 | 11 | 5 | 5 | 5 | 11 | 11 | 11 | 5 | 5 | 5
Duct Location | Insulation R (m2·K)/W | 0 | 0.7 | 1.4 | 0 | 0.7 | 1.4 | 0 | 0.7 | 1.4 | 0 | 0.7 | 1.4
Conditioned space | a | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Attic | C | 1.26 | 0.71 | 0.63 | 0.68 | 0.33 | 0.27 | 1.02 | 0.66 | 0.60 | 0.53 | 0.29 | 0.25
Attic | H/F | 0.49 | 0.29 | 0.25 | 0.34 | 0.16 | 0.13 | 0.41 | 0.26 | 0.24 | 0.27 | 0.14 | 0.12
Attic | H/HP | 0.56 | 0.37 | 0.34 | 0.34 | 0.19 | 0.16 | 0.49 | 0.35 | 0.33 | 0.28 | 0.17 | 0.15
Basement | C | 0.12 | 0.09 | 0.09 | 0.07 | 0.05 | 0.04 | 0.11 | 0.09 | 0.09 | 0.06 | 0.04 | 0.04
Basement | H/F | 0.28 | 0.18 | 0.16 | 0.19 | 0.10 | 0.08 | 0.24 | 0.17 | 0.15 | 0.16 | 0.09 | 0.08
Basement | H/HP | 0.23 | 0.17 | 0.16 | 0.14 | 0.09 | 0.08 | 0.20 | 0.16 | 0.15 | 0.12 | 0.08 | 0.07
Crawlspace | C | 0.16 | 0.12 | 0.11 | 0.10 | 0.06 | 0.05 | 0.14 | 0.12 | 0.11 | 0.08 | 0.06 | 0.05
Crawlspace | H/F | 0.49 | 0.29 | 0.25 | 0.34 | 0.16 | 0.13 | 0.41 | 0.26 | 0.24 | 0.27 | 0.14 | 0.12
Crawlspace | H/HP | 0.56 | 0.37 | 0.34 | 0.34 | 0.19 | 0.16 | 0.49 | 0.35 | 0.33 | 0.28 | 0.17 | 0.15

## Table
| N | Y
1 | 1.17 | 0.86
2 | 1.45 | 0.85
3 | 2.07 | 0.92
4 | 3.67 | 1.24

## R_values
Component | ID | Thickness [mm] | R [m2 · C/W]
Outside surface (winter) | out_winter |  | 0.03
Outside surface (summer) | out_summer |  | 0.044
Inside surface, still air | ins |  | 0.12
Plane air space, vertical, ordinary surfaces (eeff 0,82): | air_space_13 | 13 | 0.16
| air_space_20 | 20 | 0.17
| air_space_40 | 40 | 0.16
| air_space_90 | 90 | 0.16
Insulation, 25 mm (1 in): | glass_fiber | 25 | 0.7
| mineral_fiber | 25 | 0.66
| urethane | 25 | 0.98
Stucco, 25 mm (1 in) | stucco | 25 | 0.037
Face brick, 100 mm (4 in) | face_brick | 100 | 0.075
Common brick, 100 mm (4 in) | com_brick | 100 | 0.12
Steel siding | metal |  | 0
Slag, 13 mm (21 in) | slag | 13 | 0.067
Wood, 25 mm (1 in) | wood | 25 | 0.22
Wood stud, nominal 2 in 4 in (3,5 in or 90 mm wide) | wood_stud_2.4 | 90 | 0.63
Wood stud, nominal 2 in 6 in (5,5 in or 140 mm wide) | wood_stud_2.6 | 140 | 0.98
Clay tile, 100 mm (4 in) | tile | 100 | 0.18
Acoustic tile | acoustic_tile | 200 | 0.32
Asphalt shingle roofing | asphalt | 200 | 0.077
Building paper | paper | 1 | 0.011
Concrete block, 100 mm (4 in): | block_lightweight | 100 | 0.27
| block_heavyweight | 100 | 0.13
Plaster or gypsum board, 13 mm (21 in) | gypsum | 13 | 0.079
Wood fiberboard, 13 mm (21 in) | wood_fiber | 13 | 0.23
Plywood, 13 mm (21 in) | plywood | 13 | 0.11
Concrete, 200 mm (8 in): | concrete_hightweight | 200 | 1.17
| concrete_heavyweight | 200 | 0.12
Cement mortar, 13 mm (1/2 in) | cement | 13 | 0.018
Wood bevel lapped siding, 13 mm 200 mm (1/2 in 8 in) | wood_bevel | 13 | 0.14
elastomeric coating | coating | 2 | 0

## Alpha_values
Material | ID | white | light | medium | dark
asphalt shingles | asphalt | 0.75 | 0.75 | 0.85 | 0.92
tile | tile | 0.3 | 0.4 | 0.8 | 0.8
metal | metal | 0.35 | 0.5 | 0.7 | 0.9
elastomeric coating | coating | 0.3

## SLF
0 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
N | 2.8 | 2.1 | 1.4 | 1.5 | 1.7 | 1.0 | 0.8 | 0.9 | 0.8
NE | 1.4 | 1.5 | 1.6 | 1.2 | 1.3 | 1.3 | 0.9 | 0.9 | 0.8
NW | 1.4 | 1.5 | 1.6 | 1.2 | 1.3 | 1.3 | 0.9 | 0.9 | 0.8
E | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.0 | 1.0 | 0.9 | 0.8
W | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.0 | 1.0 | 0.9 | 0.8
SE | 2.1 | 1.8 | 2.0 | 1.7 | 1.5 | 1.6 | 1.4 | 1.2 | 1.1
SW | 2.1 | 1.8 | 2.0 | 1.7 | 1.5 | 1.6 | 1.4 | 1.2 | 1.1
S | 20.0 | 14.0 | 6.9 | 4.7 | 3.3 | 2.7 | 2.1 | 1.7 | 1.4
INTERIOR ATENUATION COEFFCIENTS IACcl
SOLAR LOAD FACTORS SLF |  |  | Layers | Glazing Type | Light-Open | Dark Closed | Light Closed
Exposure | Single Family Detached |  | 1 | 1 | 0.64 | 0.71 | 0.45
N | 0.44 |  | 1 | 2 | 0.68 | 0.72 | 0.50
NE | 0.21 |  | 2 | 1 | 0.72 | 0.81 | 0.57
E | 0.31 |  | 2 | 3 | 0.76 | 0.86 | 0.64
SE | 0.37 |  | 2 | 4 | 0.79 | 0.88 | 0.68
S | 0.47 |  | 2 | 2 | 0.73 | 0.82 | 0.59
SW | 0.58
W | 0.56
NW | 0.46
H | 0.58

## IRRADIANCE
[5 empty] | ED | [9 empty] | Ed
0 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | Latitude | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
N | 125 | 106 | 92 | 84 | 81 | 85 | 96 | 112 | 136 | N | 128 | 115 | 103 | 93 | 84 | 76 | 69 | 62 | 55
NE | 460 | 449 | 437 | 425 | 412 | 399 | 386 | 374 | 361 | NE | 177 | 169 | 162 | 156 | 151 | 147 | 143 | 140 | 137
NW | 460 | 449 | 437 | 425 | 412 | 399 | 386 | 374 | 361 | NW | 177 | 169 | 162 | 156 | 151 | 147 | 143 | 140 | 137
E | 530 | 543 | 552 | 558 | 560 | 559 | 555 | 547 | 537 | E | 200 | 196 | 193 | 190 | 189 | 188 | 187 | 187 | 187
W | 530 | 543 | 552 | 558 | 560 | 559 | 555 | 547 | 537 | W | 200 | 196 | 193 | 190 | 189 | 188 | 187 | 187 | 187
SE | 282 | 328 | 369 | 405 | 436 | 463 | 485 | 503 | 517 | SE | 204 | 203 | 203 | 204 | 205 | 207 | 210 | 212 | 215
SW | 282 | 328 | 369 | 405 | 436 | 463 | 485 | 503 | 517 | SW | 204 | 203 | 203 | 204 | 205 | 207 | 210 | 212 | 215
S | 0 | 60 | 139 | 214 | 283 | 348 | 408 | 464 | 515 | S | 166 | 193 | 196 | 200 | 204 | 209 | 214 | 219 | 225
H | 845 | 840 | 827 | 806 | 776 | 738 | 691 | 637 | 574 | H | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170

## OF_values
Surface Type | Surface ID | OFt | OFr
Ceiling or wall adjacent to vented attic | Ceiling_adjacent | 0.62 | -0.19
Ceiling/roof assembly | ceiling_assempbly | 1 | -0.36
Wall (wood frame) or door with solar exposure | wall_exposed | 1 | -0.36
Wall (wood frame) or door (shaded) 1 0 –0.36 | wall_shaded | 1 | -0.36
Floor over ambient | floor_over_ambient | 1 | -0.06
Floor over crawlspace | floor_over_crawlspace | 0.33 | -0.28

## TOTAL
HEATING |  |  | COOLING
Q_OPAQUE |  | [W] | Q_OPAQUE |  | [W]
Q_WINDOWS |  | [W] | Q_WINDOWS |  | [W]
Q_BELOW |  | [W] | Q_BELOW | 0 | [W]
Q_INtERNALGAIN | 0 | [W] | Q_INTERNALGAIN |  | [W]
Q_INFVEN |  | [W] | Q_INFVEN |  | [W]
Q_DISTRIBUTION |  | [W] | Q_DISTRIBUTION |  | [W]
Q_sensible_TOTAL |  | [W] | Q_sensible_TOTAL |  | [W]
Q_latent | 0 | [W] | Q_latent |  | [W]